## Calculator
PV Power Calculator Example | Field Measurements
Product specifications
Recommended input
Onsite display
Percent variation from prediction
System performance measurements | Input
Identify Inverter or String
Inverter power
DC voltage
DC current
Measured array DC watts | 0
AC voltage
AC current
Measured AC watts | 0
Watts/sq m in array plane
Cell Temperature
System STC Specifications | Input
Module STC Watts
Module STC Temp
Temperature coefficient for voltage % / deg. C
Number of modules
Array STC watts | 0
DC performance calculation | Input | Multiplier | Calculated
Array STC watts | 0 | - | -
Irradiance correction | - | 0 | 0
Temperature correction | - | #DIV/0! | #DIV/0!
Power point voltage mismatch in percent | 3 | 0.97 | #DIV/0!
Manufacturers power tolerance in percent (If +5 -5 enter 10) (the formula uses 10% of the power tolerance for the de-rate) | 5 | 0.995 | #DIV/0!
Dirt | 0 | 1 | #DIV/0!
Wiring voltage drop | 2 | 0.98 | -
Predicted DC performance for operating conditions in Watts | - | - | #DIV/0!
Comparison of predicted DC performance to measurements |  | Calculated
Actual DC performance from measurements in Watts |  | 0
Predicted DC performance for operating conditions in Watts |  | #DIV/0!
Actual DC performance as a percentage |  | #DIV/0!
AC performance calculation | Input | Multiplier | Calculated
Predicted DC performance for operating conditions in Watts | - | - | #DIV/0!
Inverter CEC rated efficiency |  | 0 | -
Predicted AC performance for operating conditions Watts | - | - | #DIV/0!
Comparison of predicted AC performance to measurements |  | Calculated
Actual AC performance from measurements in Watts |  | 0
Predicted AC performance for operating conditions Watts |  | #DIV/0!
Actual AC performance as a percentage |  | #DIV/0!

## Calculator - Example
PV Power Calculator Example | Field Measurements
Product specifications
Recommended input
Onsite display
Percent variation from prediction
System performance measurements | Input
Identify Inverter or String | Sample A
Inverter power | 1692
DC voltage | 280
DC current | 9.5
Measured array DC watts | 2660
AC voltage | 240
AC current | 9.6
Measured AC watts | 2304
Watts/sq m in array plane | 920
Cell Temperature | 45
System STC Specifications | Input
Module STC Watts | 300
Module STC Temp | 25
Temperature coefficient for voltage % / deg. C | -0.44
Number of modules | 10
Array STC watts | 3000
DC performance calculation | Input | Multiplier | Calculated
Array STC watts | 3000 | - | -
Irradiance correction | - | 0.92 | 2760
Temperature correction | - | 0.978 | 2699.28
Power point voltage mismatch in percent | 3 | 0.97 | 2618.3016
Manufacturers power tolerance in percent (If +5 -5 enter 10) (the formula uses 10% of the power tolerance for the de-rate) | 5 | 0.995 | 2605.2101
Dirt | 0 | 1 | 2605.2101
Wiring voltage drop | 2 | 0.98 | -
Predicted DC performance for operating conditions in Watts | - | - | 2553.1059
Comparison of predicted DC performance to measurements |  | Calculated
Actual DC performance from measurements in Watts |  | 2660
Predicted DC performance for operating conditions in Watts |  | 2553.1059
Actual DC performance as a percentage |  | 104.1868
AC performance calculation | Input | Multiplier | Calculated
Predicted DC performance for operating conditions in Watts | - | - | 2553.1059
Inverter CEC rated efficiency | 92 | 0.92 | -
Predicted AC performance for operating conditions Watts | - | - | 2348.8574
Comparison of predicted AC performance to measurements |  | Calculated
Actual AC performance from measurements in Watts |  | 2304
Predicted AC performance for operating conditions Watts |  | 2348.8574
Actual AC performance as a percentage |  | 98.0902